## Sheet1
lesson_id | mistake | reason | resolution | discipline | project_type | phase | date | vendor
LESSON_0001 | Electrical conduit installed before structural framing complete | Poor coordination between electrical and structural teams. Schedule pressure led to premature installation. | Conduit had to be relocated after framing. Implemented mandatory coordination meetings every Monday. | Electrical | Commercial | Construction | 2024-03-15 | ABC Electric
LESSON_0002 | Mechanical HVAC ductwork clashed with sprinkler piping | 3D coordination model was not updated with latest sprinkler revisions | Redesigned duct routing in field. Now require BIM updates within 48 hours of any change. | Mechanical | Industrial | Construction | 2024-02-20 | Cool Air Systems
LESSON_0003 | Civil grading did not account for required drainage slopes | Site survey data was outdated by 6 months. Ground conditions had changed. | Re-graded entire site. Now require fresh survey within 30 days of mobilization. | Civil | Infrastructure | Construction | 2024-01-10
LESSON_0004 | Instrumentation cables pulled before cable tray was inspected | Contractor started work before receiving QC approval due to schedule pressure | Some cables had to be re-pulled. Implemented hard stop: no work without QC signoff. | Instrumentation | Industrial | Construction | 2024-04-05 | Precision Controls Inc
LESSON_0005 | Electrical panel locations conflicted with door swing clearances | Panel locations were designed without field verification of actual door hardware | Panels relocated at significant cost. Now require field verification during design phase. | Electrical | Commercial | Design | 2023-11-30
LESSON_0006 | Piping supports designed for wrong load conditions | Design assumed empty pipe weight, did not account for fluid density during operation | All supports had to be reinforced. Added load calculation review checklist. | Piping | Industrial | Design | 2024-02-28
LESSON_0007 | Control system programming started before final P&IDs approved | Programming team wanted to get ahead of schedule, assumed P&IDs wouldn't change | 30% of logic had to be rewritten. Now enforce design freeze before programming starts. | Controls | Industrial | Design | 2024-03-20 | AutomationPro
LESSON_0008 | Structural steel arrived 3 weeks late causing project delay | Vendor was not given formal notice to proceed, operated on verbal authorization only | Implemented formal PO and NTP system. All vendors now require written authorization. | Structural | Commercial | Procurement | 2024-01-25 | SteelCo Industries
LESSON_0009 | Commissioning revealed 40% of instrumentation out of calibration | Instruments sat in warehouse for 8 months before installation. Calibration dates expired. | All instruments recalibrated. Now track calibration dates in procurement system. | Instrumentation | Industrial | Commissioning | 2024-04-15 | Precision Controls Inc
LESSON_0010 | HVAC system failed to maintain temperature during startup | Design calculations used incorrect outdoor air temperature assumptions | Added supplemental cooling capacity. Now require site-specific weather data for all HVAC designs. | Mechanical | Commercial | Startup | 2024-05-01 | Cool Air Systems